## README
topic | how it works
What this file is | All inputs of GreenLCC India for one building. Edit the values, save, then open the file from the tool's Home page.
Project sheet | One row per input. Type values in the 'value' column only; % fields are typed as percent (8 = 8%).
Measures sheet | One row per green option. Costs and savings are INCREMENTAL over the code-minimum option it replaces (e.g. VRF capex = VRF price − price of the split ACs it replaces).
Groups | Rows sharing a Group are alternatives (one HVAC system, one solar size): the optimizer picks at most one per group.
Life and part | A measure is re-bought when its life ends inside the study period; its one replaceable part is re-bought every part life. Unused life at the end is credited back as salvage (planning-horizon method).
IGBC sheets | Credits: 'fixed' credits add the Fixed points of the measures that claim them; 'threshold_pct' credits score the combined % saving (energy_eff, energy_re or water) against thresholds written as pct:points¦pct:points. Levels: points needed for each rating.
Fixed constants | Roof area per kWp = 10 m²; solar export credit escalation = 0%.
Status of the demo data | Prices and tariffs are realistic estimates with sources in the Project/Measures notes; IGBC point tables are illustrative.
Measures column: ID | Short unique code, e.g. PV_100
Measures column: Measure | Plain name
Measures column: Group | Options with the same group are alternatives: at most one is chosen. Blank = independent
Measures column: IGBC credit | Credit the measure contributes to (from IGBC_credits)
Measures column: Fixed points (points) | Only for 'fixed' credits; threshold credits are scored from the savings
Measures column: Capex (incremental) (₹) | Price above the code-minimum option it replaces, year 0
Measures column: Life (years) | Service life; re-bought when it ends inside the study period, salvage counted at the end
Measures column: O&M, year 1 (incremental) (₹/yr) | Extra maintenance vs baseline; escalates with inflation
Measures column: Energy saved (kWh/yr) | Electricity saved vs baseline (efficiency measures)
Measures column: Solar size (kWp) | Rooftop solar capacity (solar measures only)
Measures column: Water saved (kL/yr) | Water saved vs baseline
Measures column: Degradation (%/yr) | Yearly loss of savings or solar output
Measures column: Replaceable part | One major part with a shorter life (inverter, compressor…), optional
Measures column: Part cost (₹) | Today's price of that part
Measures column: Part life (years) | How often the part is replaced
Measures column: Notes / basis | How the numbers were sized; source

## Project
field | input | value | unit | meaning | source / status
name | Project name | Pune Tech Office (demo) |  | Shown on every page and in the report | Illustrative building, not a real project
city | City | Pune |  | Shown in the report header
roof_area_m2 | Usable roof area | 2500 | m² | Caps rooftop solar at roof ÷ 10 m² per kWp | Assumption: ~40% of a 6,000 m² roof plate free of plant and shading
baseline_energy_kwh | Baseline electricity use | 1800000 | kWh/yr | Code-minimum building; % savings for IGBC are measured against it | Assumption: 150 kWh/m²·yr × 12,000 m²; typical of a code-minimum Indian office (BEE star-label range)
baseline_water_kl | Baseline water use | 14000 | kL/yr | Code-minimum building; % water saving for IGBC | Assumption: 1,000 occupants × 45 L/day × 300 days (NBC 2016 office norm)
study_period | Study period (planning horizon) | 25 | years | Common analysis period N for every alternative (Ch 5) | Choice: 25 years = PV module life, a common LCCA horizon
discount_rate | MARR (discount rate, nominal) | 10 | % | Minimum attractive rate of return used to discount every cash flow (Ch 7) | Assumption: private developer MARR ≈ 10-yr G-sec (~6.5%) + 3–4 pp risk premium
inflation | General inflation | 5 | % | Escalates O&M and re-purchase prices; real MARR = (1+MARR)/(1+inflation) − 1 (Ch 2) | Assumption: RBI CPI target 4% ± 2 pp; long-run average ~5%
grid_tariff | Grid tariff, year 1 | 13 | ₹/kWh | All-in price of a kWh bought from the grid | Estimate (verify, Q-003): MSEDCL commercial >50 kW energy charge ~₹12–15/kVAh plus wheeling and FAC; MERC 2025 MYT order under review
tariff_escalation | Tariff escalation | 5 | %/yr | Expected yearly growth of the grid tariff (geometric gradient) | Assumption: Maharashtra commercial tariffs have risen ~4–6% a year
tariff_escalation_sd | Tariff escalation uncertainty (1 sd) | 2 | %/yr | Spread of tariff growth used by the Monte Carlo | Assumption: ±2 pp covers regulatory swings like the 2025 MERC order and its review
export_tariff | Solar export credit | 2.82 | ₹/kWh | Paid for solar kWh exported to the grid (held flat) | Source: MERC rooftop-solar export credit ₹2.82/kWh, FY 2025-26 (SolarQuarter, Apr 2025)
water_tariff | Water + sewage tariff, year 1 | 60 | ₹/kL | Price of a kL of water saved | Assumption: Pune commercial water + sewerage, ~₹50–70/kL (higher if tankers are used)
water_escalation | Water tariff escalation | 6 | %/yr | Expected yearly growth of the water tariff | Assumption
pv_yield_kwh_per_kwp | Solar specific yield | 1450 | kWh/kWp/yr | Year-1 output of one kWp at this site | Assumption: Pune ~1,400–1,500 kWh/kWp/yr (typical PVGIS/NREL estimates)
pv_self_consumption | Solar self-consumption share | 95 | % | Share of solar used on site (worth the grid tariff); the rest is exported | Assumption: office daytime load (>200 kW) absorbs almost all output; export mainly on holidays
grid_emission_factor | Grid emission factor | 0.727 | tCO₂/MWh | CO₂ avoided per MWh not drawn from the grid | Source: CEA CO₂ Baseline Database v20 (FY 2023-24), weighted average 0.727 tCO₂/MWh
target_level | Target IGBC level | Gold |  | Must match a level in the IGBC_levels sheet | Choice
base_points | IGBC points already earned by the base design | 52 | points | Credits the design earns without any measure below | Illustrative: points the base design earns without the measures below

## Measures
ID | Measure | Group | IGBC credit | Fixed points | Capex (incremental) | Life | O&M, year 1 (incremental) | Energy saved | Solar size | Water saved | Degradation | Replaceable part | Part cost | Part life | Notes / basis
HVAC_VRF | VRF air conditioning (350 TR) | HVAC | EE-C2 | 0 | 15750000 | 15 | 175000 | 248000 | 0 | 0 | 0.5 |  | 0 | 0 | Installed ~₹90k/TR vs split/packaged baseline ~₹45k/TR; ISEER ~5.8 vs 3.8 ≈ 25% of HVAC kWh; AMC +₹500/TR/yr
HVAC_CHILLER | Water-cooled chiller plant (350 TR) | HVAC | EE-C2 | 0 | 24500000 | 25 | 900000 | 346000 | 0 | 0 | 0.5 | Cooling tower and pump overhaul | 3500000 | 12 | Installed ~₹1.15 L/TR incl. towers, pumps, AHUs; plant ~0.85 kW/TR vs ~1.3 ≈ 35% of HVAC kWh; operators + water treatment ₹9 L/yr
GLZ_DGU | Double-glazed units (3,000 m²) | GLAZING | EE-C2 | 0 | 7500000 | 30 | 0 | 30000 | 0 | 0 | 0 |  | 0 | 0 | +₹2,500/m² over single glazing; lower U-value ≈ 3% of HVAC kWh
GLZ_LOWE | Low-e double-glazed units (3,000 m²) | GLAZING | IEQ-C1 | 2 | 13500000 | 30 | 0 | 69000 | 0 | 0 | 0 |  | 0 | 0 | +₹4,500/m² over single glazing; SHGC 0.25 cuts solar gain ≈ 7% of HVAC kWh; better daylight earns IEQ points
LIGHT_LED | LED lighting + occupancy/daylight sensors |  | EE-C4 | 3 | 5400000 | 12 | 0 | 108000 | 0 | 0 | 1 |  | 0 | 0 | +₹450/m² over code-minimum fixtures; LPD and controls ≈ 30% of lighting kWh; drivers ~12 yrs
BMS | Energy sub-metering + BMS |  | EE-C5 | 1 | 4800000 | 15 | 250000 | 59000 | 0 | 0 | 0 |  | 0 | 0 | ~₹400/m²; scheduling and set-point control ≈ 6% of HVAC kWh; software/AMC ₹2.5 L/yr
COOLROOF | Cool roof coating (2,500 m²) |  | SS-C3 | 2 | 750000 | 10 | 15000 | 15000 | 0 | 0 | 2 |  | 0 | 0 | High-SRI coating ~₹300/m², recoat every 10 yrs; ~6 kWh/m² of roof saved on top-floor cooling; soiling 2%/yr
PV_100 | Rooftop solar 100 kWp | PV | EE-C3 | 0 | 4500000 | 25 | 60000 | 0 | 100 | 0 | 0.5 | Inverters | 500000 | 12 | ₹45,000/kWp (MSEDCL 2026 rooftop benchmark ₹45,450/kW; market ₹38–50k); O&M ₹600/kWp/yr; inverters ₹5,000/kWp every 12 yrs; 0.5%/yr module degradation
PV_150 | Rooftop solar 150 kWp | PV | EE-C3 | 0 | 6750000 | 25 | 90000 | 0 | 150 | 0 | 0.5 | Inverters | 750000 | 12 | ₹45,000/kWp (MSEDCL 2026 rooftop benchmark ₹45,450/kW; market ₹38–50k); O&M ₹600/kWp/yr; inverters ₹5,000/kWp every 12 yrs; 0.5%/yr module degradation
PV_200 | Rooftop solar 200 kWp | PV | EE-C3 | 0 | 9000000 | 25 | 120000 | 0 | 200 | 0 | 0.5 | Inverters | 1000000 | 12 | ₹45,000/kWp (MSEDCL 2026 rooftop benchmark ₹45,450/kW; market ₹38–50k); O&M ₹600/kWp/yr; inverters ₹5,000/kWp every 12 yrs; 0.5%/yr module degradation
WTR_FIX | Low-flow fixtures (taps, dual-flush WCs) |  | WE-C1 | 0 | 1200000 | 12 | 10000 | 0 | 0 | 3500 | 0 |  | 0 | 0 | ~200 fixtures × ₹6,000 extra; ≈ 25% of baseline water
WTR_STP | STP with treated-water reuse (50 KLD) |  | WE-C2 | 2 | 4000000 | 20 | 450000 | 0 | 0 | 4900 | 0 | Blowers, pumps and membranes | 800000 | 7 | 50 KLD plant ~₹40 L; operator, power, chemicals ₹4.5 L/yr; reuse for flushing and landscape ≈ 35% of water

## IGBC_credits
credit_id | category | name | max_points | rule | basis | thresholds | mandatory
EE-C2 | Energy Efficiency | Enhanced energy performance | 11 | threshold_pct | energy_eff | 5:1¦10:3¦15:5¦20:7¦25:9¦30:11 | FALSE
EE-C3 | Energy Efficiency | On-site renewable energy | 8 | threshold_pct | energy_re | 2:2¦5:4¦10:6¦15:8 | FALSE
EE-C4 | Energy Efficiency | Efficient lighting and controls | 3 | fixed |  |  | FALSE
EE-C5 | Energy Efficiency | Energy metering and BMS | 1 | fixed |  |  | FALSE
WE-C1 | Water Efficiency | Water-efficient fixtures and reuse | 4 | threshold_pct | water | 15:1¦30:2¦45:3¦60:4 | TRUE
WE-C2 | Water Efficiency | Wastewater treatment and reuse | 2 | fixed |  |  | FALSE
SS-C3 | Site and Planning | Heat island reduction (cool roof) | 2 | fixed |  |  | FALSE
IEQ-C1 | Indoor Environment | Daylight and glazing performance | 2 | fixed |  |  | FALSE

## IGBC_levels
level | min_points | rank
Certified | 50 | 1
Silver | 60 | 2
Gold | 70 | 3
Platinum | 80 | 4